BUTTERFLY VALVES WAFER TYPE

Butterfly valves, wafer type PN10 or PN16, depending on the needs of the project, with cast iron body GG25 with length according to EN 558-1 series 20, stainless steel disc CF8M (1.4408) and interchangeable liner EPDM (or NBR, FKM,… depending on the needs of the project).

The body of the valves shall have four built-in guide lugs for centering the valves between flanges according to EN1092 PN6/10/16 and ANSI cl.150. The design of the body and the liner will ensure, with special notches in the center and at the sides, the stable positioning of the liner on the body.

Up to dimension DN300 (DN125 for PN16), the valves shall have 2-piece stainless steel AISI 304 shaft, to reduce flow restriction. For larger dimensions the shaft shall be single piece and will pass through the disk. The upper part of the shaft shall be mounted on two brass bearings and there shall be two sealing o-rings. To secure the shaft against accidental extraction, during any removal of the actuator, there shall be a safety screw which will enter into a special slot in the shaft.

The valves shall be operated by a handle that clicks every 6th (15 positions) or by a permanently lubricated reducer with hand-wheel, depending on the application.

In order to ensure the possibility of future automation of the valves, the dimensions of the actuator adaptation (square upper shaft and actuator flange) shall be in accordance with EN5211, as per the following table:

DN 		Square		Flange

50-65		 11mm 		F04

80-125	 14mm 		F05

150-200	 17mm 		F07

250-300	 22mm 		F10

The valves shall be zero leakage tight, according to EN 12266 (leakage rate A)

The valves must come from a European Union manufacturer, comply with PED 2014/68/EU Modul D and be approved by an internationally accredited certification body.

The manufacturer of the valves must be certified in accordance with ISO 9001: 2015.

Indicative type: Z011-A by EBRO

BUTTERFLY VALVES WAFER TYPE PN10 for POTABLE WATER

Butterfly valves, wafer type PN10, depending on the needs of the project, with length according to EN 558-1 series 20, with cast iron body GG25, stainless steel disc CF8M (1.4408) and interchangeable liner EPDM.

The body of the valves shall have four built-in guide lugs for centering the valves between flanges according to EN1092 PN6/10/16 and ANSI cl.150. The design of the body and the liner will ensure, with special notches in the center and at the sides, the stable positioning of the liner on the body

Up to size DN300, the valves shall have 2-piece stainless steel AISI 304 shaft, to reduce flow restriction. For larger dimensions the shaft shall be single piece and will pass through the disk. The upper part of the shaft shall be mounted on two brass bearings and there shall be two sealing o-rings. To secure the shaft against accidental extraction, during any removal of the actuator, there shall be a safety screw which will enter into a special slot in the shaft.

The valves shall be operated by a handle that clicks every 6th (15 positions) or by a permanently lubricated reducer with hand-wheel, depending on the application.

In order to ensure the possibility of future automation of the valves, the dimensions of the actuator adaptation (square upper shaft and actuator flange) shall be in accordance with EN5211, as per the following table:

DN 		Square		Flange

50-65		 11mm 		F04

80-125	 14mm 		F05

150-200	 17mm 		F07

250-300	 22mm 		F10

The valves shall be zero leakage tight, according to EN 12266 (leakage rate A)

The valves must come from a European Union manufacturer, comply with PED 2014/68/EU Modul D and have DVGW and WRAS certification for their suitability for use in drinking water networks.

The manufacturer of the valves must be certified in accordance with ISO 9001: 2015.

Indicative type: Z011-A by EBRO

BUTTERFLY VALVES WAFER TYPE PN16 for POTABLE WATER

Butterfly valves, wafer type PN16, depending on the needs of the project, with length according to EN 558-1 series 20, with cast iron body GG25, stainless steel disc CF8M (1.4408) and interchangeable liner EPDM.

The body of the valves will have four built-in guide lugs for centering the valves between flanges according to EN1092 PN6/10/16 and ANSI cl.150. The design of the body and the liner will ensure, with special notches in the center and at the sides, the stable positioning of the liner on the body

Up to size DN125, the valves will have 2-piece stainless steel AISI 304 shaft, to reduce flow restriction. For larger dimensions the shaft will be single piece and will pass through the disk. The upper part of the shaft shall be mounted on two brass bearings and there will be two sealing o-rings. To secure the shaft against accidental extraction, during any removal of the actuator, there will be a safety screw which will enter into a special slot in the shaft.

The valves shall be operated by a handle that clicks every 6th (15 positions) or by a permanently lubricated reducer with hand-wheel, depending on the application.

In order to ensure the possibility of future automation of the valves, the dimensions of the actuator adaptation (square upper shaft and actuator flange) shall be in accordance with EN5211, as per the following table:

DN 		Square		Flange

50-65		 11mm 		F04

80-125	 14mm 		F05

150-200	 17mm 		F07

250-300	 22mm 		F10

The valves will be zero leakage tight, according to EN 12266 (leakage rate A)

The valves must come from a European Union manufacturer, comply with PED 2014/68/EU Modul D and have DVGW and WRAS certification for their suitability for use in drinking water networks.

The manufacturer of the valves must be certified in accordance with ISO 9001: 2015.

Indicative type: Z011-A by EBRO